## Cover
Gotion ESS — Modbus point export
Project | Site-17 Lab BESS
PCS | Sinexcel PWS1725K
BMS firmware | v3.2.1
NOTE | Map is on sheet BMS_Map

## BMS_Map
Protocol Offset | Reg Type | Tag Name | R/W | Type | Gain | Unit | Comment
256 | 4x Holding | Stack_Voltage | R | U16 | 0.1 | V | 电池总电压
257 | 4x Holding | Stack_Current | R | S16 | 0.1 | A | signed
258 | 4x Holding | Work_State | R | U16 | 1 |  | 0=standby 1=dischg 2=chg
259 | 4x Holding | SOC | R | U16 | 1 | %
260 | 4x Holding | SOH | R | U16 | 1 | %
261 | 4x Holding | Max_Cell_mV | R | U16 | 1 | mV
262 | 4x Holding | Min_Cell_mV | R | U16 | 1 | mV
270 | 4x Holding | Insulation_kOhm | R | U16 | 1 | kOhm
285 | 4x Holding | Charge_Request | R | U16 | 1 |  | 1=need charge

## Alarms
Bit | Alarm text
0 | BMS comm fault
1 | Cell OV